## Asset Checklist
* = Mandatory fields
This template is required if property asset checklist is required to be updated via the mobile app for FM servicing.
The unique asset checklist | The checklist item details | Indicate the checklist entry value. Valid options includes; a) Yes/No b) Yes/No/NA c) Number d) Text e) DateTime f) Header g) SubHeader Note: Header/SubHeader are used to perform display group. | Indicates if checklist is active for usage by user in system. Enter "Y" as default
Checklist Name [100]* | Item Description [300]* | Value Type [50]* | Active (Y/N) [1]*
Chiller Servicing | Model No: | Text | Y
Chiller Servicing | IDENTIFICATION | Header | Y
Chiller Servicing | ACTIVE CHILLER WATER SETPOINT (ºc)(6 - 7.2 ºc) | Yes/No | Y
Chiller Servicing | CHILLER WATER SUPPLY TEMP (ºc)(6 - 8.0 ºc) | Yes/No | Y
Chiller Servicing | CHILLER WATER RETURN TEMP (ºc)(10 - 14 ºc) | Number | Y
Chiller Servicing | CONDENSER WATER SUPPLY TEMP ( ºc)(26 - 31 ºc ) | Number | Y
Chiller Servicing | CONDENSER WATER RETURN TEMP ( ºc)(32 - 36 ºc) | Number | Y
Chiller Servicing | REFRIGARANT | Header | Y
Chiller Servicing | EVAPORATOR REF PRESSURE (kpa)(-53 to -59 Kpa) | Number | Y
Chiller Servicing | CONDENSING REF PRESSURE (kpa)(17-24 Kpa) | Number | Y
Chiller Servicing | EVPORATOR SATURATED REF TEMPERATURE (ºc)(6.0 - 7.0 ºc) | Number | Y
Chiller Servicing | CONDENSER SATURATED REF TEMPERATURE (ºc)(34 - 40 ºc) | Number | Y
Chiller Servicing | COMPRESSOR | Header | Y
Chiller Servicing | OIL SUMP/TANK TEMPERATURE (ºc)(48 - 60 ºc) | Number | Y
Chiller Servicing | DIFFERENTIAL OIL PRESSURE (Kpa)(130 to 190 Kpa) | Number | Y
Chiller Servicing | OIL LEVEL SIGHTGLASS (mm)(1/2 - FULL) | Text | Y
Chiller Servicing | CHILLER PHASE AMPERES, R (amps)(CH 1 to 4 = 35 - 90 A; CH 5 = 150 - 300 A; CH 6 = 400 - 750 A) | Number | Y
Chiller Servicing | CHILLER HOUR METER (watts) | Number | Y
Chiller Servicing | DEGREE OF GUILDE VANE OPENED ( %) | Number | Y
Chiller Servicing | Remarks | Text | Y